        EIE 07 210 EINSTEIN

EINSTEIN
Expert-system for an INtelligent Supply of Thermal Energy in INdustry

 EINSTEIN – Theoretical concepts

Draft Version 0.24

Project No.: 07-0008-EE
Internal document
Authors: Hans Schweiger, Stoyan Danov
Date: 17/12/2007

VERSIONS:

V0.01	24/09/07	HS	Adaptation from ICAEN Tool Developers manual V0.05
V0.02	02/10/07	SD	Figures and nomenclature
V0.03	03/10/07	HS,SD	Modifications figures, text, notes
V0.04	04/10/07	SD	Nomenclature, figures, notes
V0.20	06/11/07	SD	Text, nomenclature to ISO 31 (with a few exceptions)
V0.21	08/11/07	HS	Some small changes on V0.20
V0.22	08/11/07	SD	Small changes on V0.21
V0.23	12/12/07	SD	Changes in section 1, FEC, FET, CHP-PET, Figure 4, Nomenclature
V0.24	17/12/07	SD	Some small changes over V0.23
V0.25	25/03/08	CV	Correction of calculation of net and gross UPH / UPHc / Introduction of latent heat dotQ_L in UPHm

# Heat flows in industry – definitions

For the analysis of the heat demand the following quantities are used:

- Final energy consumption for thermal uses (FET): LCV of the fuel consumption for thermal use + electricity consumption for thermal use.
- Useful supply heat (USH): heat generated in the heat supply system (boilers).
- Useful process heat (UPH): heat delivered to a process (measured at the entrance of the process heat exchanger).

Figure 1. Generation and distribution of heat to processes

Figure 2. Energy flows diagram

Figure 3. Example of a washing process represented within the EINSTEIN Scheme
## Final energy consumption and primary energy consumption

### Total final energy consumption and primary energy consumption

FEC, PEC = total final and primary energy consumption
The total final energy consumption (FEC) is used to account for the total final energy that enters the factory in the form of fuels (expressed in terms of LCV), electricity and district heat.
The primary energy consumption is calculated from the electricity consumption and the consumption of the different fuels:
E_PE = f_{PE,el}E_{el} + sum_{i=1}^Nfuels f_{PE,i}E_{fuel,i}
where fPE,el (typical value: 3) is the primary energy conversion factor for electricity and fPE,i (typical value: 1.1) is the primary energy conversion factor for the different fuel types.
The total final energy consumption is the sum of the final energy consumption for the different energy sources:
E_FC = sum_{i=1}^{N_{Esources}} E_{FC,i}
where NEsources is the number of the energy sources (diffrent fuel types, electricity, etc.).
Part of the FEC is consumed for thermal uses (heating or cooling), and other part of it is consumed for non-thermal uses.
### Total final and primary energy consumption for thermal uses

FET, PET = final and primary energy consumption for thermal uses (heating & cooling)
The total final energy consumption for thermal uses is the energy (electricity and fuels) used only for heating and cooling (part of FEC). Other non-thermal uses such as lighting, motor driving, fuel for internal transport, etc. are not part of FET.
The primary energy for thermal uses is calculated similarly to the PEC (see previous section).
The total finel energy for thermal uses is the sum of the energy consumed by the heating or cooling equipment in the factory:
E_FT = sum_{j=1}^Nequip E_{FT,j}
where Nequip is the number of thermal equipment units in the factory (boilers, chillers, CHP motors, etc.)
#### Thermal conversion equipment (only)

For the simple thermal conversion equipment (boilers, chillers) the FET is equal to the consumed fuel (in terms of LCV) or electricity.
#### Combined heat and power (CHP)

For CHP equipment (reciprocating motors, turbines) the FET will be considered as the difference between the consumed fuel (in terms of LCV ) and the self-generated electricity:

E_{FT,j} = E_{fuel,j} - E_{elgen, j}

In the case of CHP equipment the PET (as calculated in section 1.1.1) is allowed to obtain negative values.

## Useful supply heat and cold (USH/C)

Useful supply heat (USH) is the heat going out of the conversion equipment (boilers, burners), measured at the outlet of the equipment (machine room).
The heat content in heat supplies that are not closed loops (e.g. steam w/o condensate recovery, direct hot water preparation and distribution is defined based on the (external) reference temperature (cold water inlet, air inlet).
Q_USH = q_{m,o} h_o - q_{m,ret} h_ret - q_{m,i} h_i
where the subindices refer to outlet (o), return (ret) and inlet (i), the latter being the external reference for open loops.
For most industries the fuel consumption (FET) is known, whereas USH/C and UPH/C had to be estimated. If no data for the conversion efficiencies of the equipment are available, the following standard values will be used as default for estimation:
· Boiler efficiency (USH/FET): 85 %
· Chiller efficiency (USC/FET): 3.0
· Overall efficiency of heat generation and distribution (UPH/FET): 70 %.

Figure 4. Sankey diagram for standard conversion efficiencies

## Useful process heat and cold (UPH/C)

### Gross and net process heat consumption

Useful (net) process heat (UPH) is considered as the total external process heat to be delivered to the process, either by the heat supply system, or by external[1] heat recovery.
[1] The distinction between an internal and external heat recovery depends on the specification of the system boundaries and is thought to be used for compact equipment with some internal heat exchangers: e.g. gross heat demand in a pasteuriser using cold milk would be the heating up from 4ºC to 72 ºC, whereas net heat demand would be only the residual heating up after heat recovery, e.g. from 57 ºC to 72 ºC.

If the internal heat recovery is added to the total process heat demand, we speak of gross useful process heat.
Q_{UPH,gross} = Q_UPH + Q_{HX,internal}
### Equivalent heat demand for cooling (EHD)

As low temperature heat sources such as solar thermal energy or waste heat from heat pumps can be used with thermally driven chillers for producing cold, sometimes it is useful to add equivalent heat consumption for cold consumption to the existing consumption of UPH. Based on a supposed thermal chiller efficiency ( %eta_tch ) the Equivalent Heat Demand for cooling can be calculated by:

Q_EHD = Q_UPC / %eta_tch

where QUPC is the Useful Process Cold demand.

 The following values will be used for conversion:
·         Overall efficiency of an absorption cooling system:             70 %
·         Mean temperature of the heat supply to the generator:       85 °C.

### Preheating of supply water for steam boilers (PSW)

Preheating of supply water (PSW) for steam boilers is a possibility for use of low temperature heat sources, additional to the possibility of direct supply to the process (part of UPH). Preheating contributes to boiler USH for covering the heat demand, thus reducing fuel consumption.
It should be taken into account that any reduction of the heat demand for the boiler (USH), reduces also the PSW (e.g. applying low temperature solar heat to process reduces the need for heat from boiler (USH), but also reduces the energy for PSW that could also be done with solar energy. This collateral effect should be accounted for. )

### Waste heat streams from processes
For the calculation of the heat recovery potential it is important to distinguish between the
total amount of waste heat and that waste heat streams that have the technical
possibility to be used.
For flows which are used as input to another process, the recoverable waste heat is
limited by the final temperature to which the flow can be cooled down.

{dot{Q}}_{UPH,w} = q_{m,o} (h_{po} - h_min)

# Temperature levels in heat supply

The temperature levels used in the analysis are the following:
·	Process temperature (PT): mean temperature of the fluid in a process.
·	Process Supply Temperature (PST): inlet temperature of the heat transport medium used for heating of the process (For example: steam temperature at the entrance of the process heat exchanger).
·	Central supply temperature (CST): temperature of the heat transport medium at the outlet of the central heat supply (boiler). The difference between CST and PST accounts for temperature losses in the distribution line.
The heat demand can be classified into different temperature intervals. The UPH usually is classified by intervals for the process temperature, whereas USH is classified by the process supply temperature.
In Table 1 is given a classification of the possible heating technologies that can be used depending on the temperature level.
Temperature interval	Temperature level of heat	Applicable heat supplying technology
< 60	Low	Heat from heat pumps or low-temperature solar thermal
< 90	Medium-low	Waste heat from CHP engines, practical limit for flat-plate solar thermal
< 150	Medium	Low pressure steam
< 250	Medium-high	SHIP limit
< 400	High	Practical limit for waste heat from gas turbines, biomass…

Table 1. Possibilities for technology application depending on temperature level.

The standard temperature intervals as given in Table 2 are used for statistical analysis of the heat demand (UPH and USH) by temperature level.
Table 1. Standard temperature intervals used in the analysis

# Process models and demand curves

## Process models

Processes in EINSTEIN are modelled using a standard process model as described in POSHIP[2]. Most processes require both heating of a fluid stream (e.g. hot air streams, hot water, renovation of water in baths, ...) and heating of some reservoir (ovens, liquid baths). The latter can be subdivided into pre-heating before the start of operation and into maintenance of temperature (compensation of thermal losses during operation).
[2] POSHIP: The Potential of Solar Heat for Industrial Processes. Project Funded by the European Commission - Directorate General for Energy and Transport. Programme ENERGIE (5th Framework Programme for Energy, Environment and Sustainable Development), Project No. NNE5-1999-0308.
The total heat demand of a process can be conceptually split into the three fractions mentioned above:
a) Circulation heat (UPHc)
The heat related with the entering medium mass flow (inflow). This is the heat needed to heat-up the entering medium to the process temperature, independently of the physical place where heat is added (prior to or within the process).
Can be defined for continuous and batch process, and is conceptually independent from the physical time interval during which the mass flow is circulating. The circulation time can be different from the operation time.
Q_{UPH,c} = m_c c_p (T_p - T_{pir})

where mc is the total mass of process medium circulating during the period under consideration (one day or one year).

The gross heat related with circulting fluid can be calculated as

Q^gross_{UPH,c} = Q_{UPH,c} + Q_{HX,internal} = m_c c_p (T_p - T_{pi})

b) Initial heating at start-up (UPHs)
The heat necessary to bring the process mass to the process temperature after process interruption (does not include heat added to bring inlet flow to process temperature in either batch or continuous process).

Q_{UPH,s} = N_s (m c_p)_e (T_p - T_s)

where (mcp)e is the effective or equivalent thermal mass of the process that consideres the thermal inertia not only of the medium itself contained within the process but also the surrounding equipment, and Ns is the number of start-ups in a given period of time.

c) Maintenance heat (UPHm)
The heat necessary to maintain process temperature. It is equivalent to the thermal losses through the process border to the ambient.

Q_{UPH,m} = [(UA)(T_p - T_env) + {dot Q}_L]t_op

where (UA) is the termal loss coefficient of the process equipment, Tenv is the environmental temperature for the process (usually the indoor temperature of the factory) and top is the process operating time.
When the value of (UA) is not known (as is the case in most real processes), it can be estimated from information about the cool-down of the process over a certain reference period (e.g during night, during weekend, or in between two baths).

T_f - T_env = (T_p - T_env) e^-(UA t_ref/m c_p)

resulting in:

UA = (m c_p/t_ref)ln[(T_p - T_env)/(T_f - T_env)]

where Tf is the final temperature after the cool-down, tref is the reference time of cool-down, (mcp) is the total thermal mass of the process, and Tp and Tenv are respectively the process and the environment temperatures.

### General model for one-medium processes

Figure 5. One-medium process model
This process is fully defined by the variables indicated in Figure 5. These are described as follows:

T(t)	Temperature of process or supply medium over time
h(t)	Specific enthalpy of process medium over time
qm(t)	Mass flow of process medium over time
mcp	Total thermal mass of process
UA	Thermal loss coefficient

Subscripts
p	process
pi	process inlet
pir	process inlet after heat recovery
po	process outlet
por	process outlet after heat recovery
i	inlet, incoming
o	outlet, outgoing
st	start-up (for temperature of process after cool-down during breaks)
ps	process supply
env	environment

Note: qm,o can be different (usually lower) than qm,i due to (a) time lags and (b) possible loss of part of the process medium (e.g.: uncontrolled evaporation).

### General model for two-medium (two in-flow/two out-flow) process

Figure 6. Two-medium process model

The two-medium process is fully defined by the variables indicated on Figure 6. These are described as follows:

T(t)	Temperature of process or supply medium over time
h(t)	Specific enthalpy of process medium over time
qm(t)	Mass flow of process medium over time
mcp	Total thermal mass of process
UA	Thermal loss coefficient

Subscripts
i1	inlet (incoming) process medium 1
i2	inlet (incoming) process medium 2
o1	outlet (outgoing) process medium 1
o2	outlet (outgoing) process medium 2
p	process
pi1	process inlet 1
pi2	process inlet 2
pi1r	process inlet 1 after heat recovery
pi2r	process inlet 2 after heat recovery
po1	process outlet 1
po2	process outlet 2
po1r	process outlet 1 after heat recovery
po2r	process outlet 2 after heat recovery
pt	process target (temperature)
s	start-up (for temperature of process after cool-down during breaks)
ps	process supply
env	environment

Note: the outgoing mass flows qm,o (1 or 2) and the composition of the media can be different from qm,i (1 or 2) due to (a) time lags and (b) possible loss of part of the process medium (e.g.: uncontrolled evaporation) or (c) mass transfer from one medium to the other (mixing or separation process).

NOTE: One unique process temperature is defined in this model for simplicity. In some cases the final temperature for the different fluid streams might be different. If this assumption is found to be limiting, it could be relaxed in the future.

### Simplifications for basic Einstein model

The general process models can be simplified assuming constant temperature levels and
mass flows:
• all inlet, set and waste heat temperatures are considered as constant.
• time dependence is only given by the schedule of the process (on/off)
For most industrial processes this constant temperature level approximation is sufficient.

## Standard demand profiles

In the following standard demand profiles for the basic EINSTEIN process models are described.

The following differnt time schedules are used:

- Schedule for the operation of the process: the time during which a constant set temperature Tp has to be maintained
- Schedule for initial heating at start-up: the time when initial heating at start-up begins.
- Schedule for incoming flows
- Schedule for outgoing flows
In the Einstein draft model there is distinguished between batch and continuous processes. The schedules of both process types are supposed to be as follows. Note that start-up phase is the first half hour within the operation period of the process. Emptying of batch processes is the first half hour after process operation.

	Continuous process	Batch process
Circulation (Inflow)	Continous during top	The first 0.5 h within top
Start-up	The first 0.5 h within top	The first 0.5 h within top
Maintenance	Continous during top	Continous during top
Evacuation of waste fluid (Outflow)	Continous during top	The first 0.5 h after top

Energy flows are expressed in

- the annual energy demand (UPHc, UPHm, UPHs, UPHw)
- the mean required heating power during yearly factory (not process !!!) operation hours

{bar {dot {Q}}}_{UPH,c,m,s,w} = Q_{UPH,c,m,s,w} over t_{op,ind}

Demand profiles f(t) are normalised so that the daily integral is equal to the daily factory operation hours, so that

Int from {0:00h} to {24:00h} f(t) dt = t_{op,ind}

Figure 7. Standard energy demand profile for continuous processes. Example: process with t_op = 2 x 4h.

Figure 8. Standard energy demand profile for batch processes. Example: process with t_op = 2 x 4h.

Nomenclature

Abbreviations and acronyms

  CST - Central Supply Temperature
  CHP - Combined Heat and Power
  EHD - Equivalent Heat Demand
  FEC - Total Final Energy Consumption
  FET - Final Energy consumption for Thermal uses
  LCV - Lower Calorific Value
  PEC - total Primary Energy Consumption
  PET – Total Primary Energy consumption for Thermal uses
  PSW - Preheating of Supply Water
  PT - Process Temperature
  ST - Supply Temperature
  UPH/C - Useful Process Heat/Cold
  USH/C - Useful Supply Heat/Cold

Symbols

  A - area, m2
  cp - specific heat capacity, J/(kg K)
  E - energy, J, (or kWh)
  f - conversion factor
  h - specific enthalpy, J/kg
  m - mass, kg
  N - number (e.g. fuels or Esources)
  Q - heat, J, (or kWh)
dot{Q} - heat flow rate, W
  qm - mass flow rate, kg/s
  T - temperature, °C
  t - time , s, (or h)
  U - global coefficient of heat transfer, W/(m2 K)
  h - efficiency, 1

Indices

  c - circulating, condensate
  cs - central supply
  e - effective
  el - electric
  elgen - self-generated electricity
  env - environment
  equip - equipment units
  EHD - equivalent heat demand
  Esources - energy sources
  f - final
  fuels - fuels
  fw - feed-up water
  FC - final energy consumption
  FT - final energy consumption for thermal use
  HX - heat recovery heat exchanger
  i - inlet, incoming, index used for energy source (fuel type, electricity)
  j - index used for thermal equipment unit
 L – latent heat (used for evaporation (+), condensation (-), endothermal or exothermal chemical reactions)
  o - outlet, outgoing
  op - operating
  p - process
  pi - process inlet
  pir - process inlet after heat recovery
  po - process otlet
  por - process outlet after heat recovery
  pt – process target
  PE - primary energy
  PS - process supply
  m - maintenance
  min - minimum
  ref – reference
  ret – return
  s - start-up (más arriba me parece que has usado st para start-up -> check consistency)
  tch - thermally driven chiller
  UPH - useful process heat
  UPC - useful process cold
  USH - useful supply heat
  USC - useful supply cold
  w - waste